## Tray
Excel Cable
Containment Sizing - Tray
Notes: | This spreadsheet is for guidance only.
This may be used for Tray only - continuous flat surface
The maximum stack height of cables on a continuous surface is 150mm.
Refer "Basket" tab of spreadsheet for non-continuous containment
[8 empty] | Cat 8 | Cat7A |  |  |  | Cat6A | [8 empty] | Cat6 | [6 empty] | Cat5e
| Enter details below |  |  | 100-903 - CAT8 - S/FTP - Dca | 100-910 - CAT7A - S/FTP - Dca | 100-912 - CAT7A+ - S/FTP - Dca | 190-910 - CAT7A - S/FTP - B2ca | 190-912 - Cat7a+ 22 AWG S/FTP - B2ca | 100-990 - CAT6A - U/FTP - Dca | 100-996 - CAT6A - F/FTP - Dca | 100-219 - CAT6A - U/UTP LSOH 23AWG - Dca | 100-914 - CAT6A - S/FTP WHITE - Dca | 100-993 - CAT6A - U/FTP EXT GRADE PE BK - Fca | 190-996 - CAT6A - F/FTP - B2ca | 190-191 - CAT6A - U/FTP LSOH - B2ca | 190-219 - CAT6A - U/UTP 23AWG - B2ca | 190-914 - CAT6A - S/FTP - B2ca | 100-071 - CAT6 - UTP - Dca | 100-076 - CAT6 - F/UTP - Dca | 100-080 - CAT6 - U/UTP 24 AWG - Dca | 100-100 - CAT6 - UTP EXT GRADE PE - Fca | 100-609 Residential CAT6 - U/UTP - Dca | 190-071 - CAT6 - UTP - B2ca | 190-076 - CAT6 - F/UTP - B2ca | 100-066 - CAT5E 4PR - UTP - Dca | 100-090 - CAT5E 4PR - UTP EXT - Fca | 100-217 - CAT5E 4PR - F/UTP LSOH - Dca | 190-066 - CAT5E 4PR - UTP - B2ca
Tray Dimensions
Width | 100 | mm | Changed
Height | 100 | mm | Diameter of Cable | 8.3 | 7.8 | 8.5 | 7.8 | 8.2 | 7.2 | 7.6 | 7 | 7.5 | 7.2 | 7.2 | 7.4 | 7 | 7.6 | 6.2 | 7.2 | 6.1 | 6.3 | 4.6 | 6.2 | 7.6 | 5.2 | 5.2 | 6.4 | 5
Spare Capacity | 99 | % | Area of Cable | 54.1061 | 47.7836 | 56.745 | 47.7836 | 52.8102 | 40.715 | 45.3646 | 38.4845 | 44.1786 | 40.715 | 40.715 | 43.0084 | 38.4845 | 45.3646 | 30.1907 | 40.715 | 29.2247 | 31.1725 | 16.619 | 30.1907 | 45.3646 | 21.2372 | 21.2372 | 32.1699 | 19.635
Area of Containment | 10000 | mm² | Number of Cables | 91 | 104 | 87 | 104 | 94 | 122 | 109 | 129 | 112 | 122 | 122 | 115 | 129 | 109 | 164 | 122 | 169 | 159 | 298 | 164 | 109 | 233 | 233 | 154 | 252
Useable Area | 9900 | mm²
Only edit blue cells
This spreadsheet is for information only. Based on EN 50174-2:2018
| NOTE: Correct at time of publication. |  |  | Rev 10: Sept 2025

## Basket
Excel Cable
Containment Sizing - Basket or Ladder
Notes: | This spreadsheet is for guidance only.
This may be used for Basket or Ladder - non-continuous surface
The maximum stack height of cables on a continuous surface is 150mm. This is reduced to 125mm for basket/ladder spacing greater than 100mm
[8 empty] | Cat 8 | Cat7A |  |  |  | Cat6A | [8 empty] | CAT 6 | [6 empty] | CAT 5E
| Enter details below |  |  | 100-903 - CAT8 - S/FTP - Dca | 100-910 - CAT7A - S/FTP - Dca | 100-912 - CAT7A+ - S/FTP - Dca | 190-910 - CAT7A - S/FTP - B2ca | 190-912 - Cat7a+ 22 AWG S/FTP - B2ca | 100-990 - CAT6A - U/FTP - Dca | 100-996 - CAT6A - F/FTP - Dca | 100-219 - CAT6A - U/UTP LSOH 23AWG - Dca | 100-914 - CAT6A - S/FTP WHITE - Dca | 100-993 - CAT6A - U/FTP EXT GRADE PE BK - Fca | 190-996 - CAT6A - F/FTP - B2ca | 190-191 - CAT6A - U/FTP LSOH - B2ca | 190-219 - CAT6A - U/UTP 23AWG - B2ca | 190-914 - CAT6A - S/FTP - B2ca | 100-071 - CAT6 - UTP - Dca | 100-076 - CAT6 - F/UTP - Dca | 100-080 - CAT6 - U/UTP 24 AWG - Dca | 100-100 - CAT6 - UTP EXT GRADE PE - Fca | 100-609 Residential CAT6 - U/UTP - Dca | 190-071 - CAT6 - UTP - B2ca | 190-076 - CAT6 - F/UTP - B2ca | 100-066 - CAT5E 4PR - UTP - Dca | 100-090 - CAT5E 4PR - UTP EXT - Fca | 100-217 - CAT5E 4PR - F/UTP LSOH - Dca | 170-066 - CAT5E 4PR - UTP - Cca | 190-066 - CAT5E 4PR - UTP - B2ca
Basket / Ladder Dimensions
Distance between supports | 100 | mm | Diameter of Cable | 8.3 | 7.8 | 8.5 | 7.8 | 8.2 | 7.2 | 7.6 | 7 | 7.5 | 7.2 | 7.2 | 7.4 | 7 | 7.6 | 6.2 | 7.2 | 6.1 | 6.3 | 4.6 | 6.2 | 7.6 | 5.2 | 5.2 | 6.4 | 5.4 | 5
Width | 100 | mm | Area of Cable | 54.1061 | 47.7836 | 56.745 | 47.7836 | 52.8102 | 40.715 | 45.3646 | 38.4845 | 44.1786 | 40.715 | 40.715 | 43.0084 | 38.4845 | 45.3646 | 30.1907 | 40.715 | 29.2247 | 31.1725 | 16.619 | 30.1907 | 45.3646 | 21.2372 | 21.2372 | 32.1699 | 22.9022 | 19.635
Height | 100 | mm | Number of Cables | 46 | 52 | 44 | 52 | 47 | 61 | 55 | 65 | 57 | 61 | 61 | 58 | 65 | 55 | 83 | 61 | 86 | 80 | 150 | 83 | 55 | 118 | 118 | 78 | 109 | 127
Spare Capacity | 50 | %
Area of Containment | 10000 | mm²
Useable Area | 5000 | mm²
Maximum Cable Stack Height | 125 | mm
| Only edit blue cells | [8 empty] | Rev 9: January 2023
This spreadsheet is for information only. Based on EN 50174-2:2018
NOTE: Correct at time of publication.

## Conduit
Excel Cable
Containment Sizing - Conduit
Notes: | This spreadsheet is for guidance only.
This may be used for Conduit
It assumes staight runs with no bends and smooth walls.
This is for INTERNAL diameter, a 25mm flexible conduit typically has a 18mm Internal diameter, please check!
[8 empty] | Cat 8 | Cat7A |  |  |  | Cat6A | [8 empty] | CAT 6 | [6 empty] | CAT 5E
| Enter details below |  |  | 100-903 - CAT8 - S/FTP - Dca | 100-910 - CAT7A - S/FTP - Dca | 100-912 - CAT7A+ - S/FTP - Dca | 190-910 - CAT7A - S/FTP - B2ca | 190-912 - Cat7a+ 22 AWG S/FTP - B2ca | 100-990 - CAT6A - U/FTP - Dca | 100-996 - CAT6A - F/FTP - Dca | 100-219 - CAT6A - U/UTP LSOH 23AWG - Dca | 100-914 - CAT6A - S/FTP WHITE - Dca | 100-993 - CAT6A - U/FTP EXT GRADE PE BK - Fca | 190-996 - CAT6A - F/FTP - B2ca | 190-191 - CAT6A - U/FTP LSOH - B2ca | 190-219 - CAT6A - U/UTP 23AWG - B2ca | 190-914 - CAT6A - S/FTP - B2ca | 100-071 - CAT6 - UTP - Dca | 100-076 - CAT6 - F/UTP - Dca | 100-080 - CAT6 - U/UTP 24 AWG - Dca | 100-100 - CAT6 - UTP EXT GRADE PE - Fca | 100-609 Residential CAT6 - U/UTP - Dca | 190-071 - CAT6 - UTP - B2ca | 190-076 - CAT6 - F/UTP - B2ca | 100-066 - CAT5E 4PR - UTP - Dca | 100-090 - CAT5E 4PR - UTP EXT - Fca | 100-217 - CAT5E 4PR - F/UTP LSOH - Dca | 170-066 - CAT5E 4PR - UTP - Cca | 190-066 - CAT5E 4PR - UTP - B2ca
Conduit Dimension
Inside Diameter | 25 | mm | Diameter of Cable | 8.3 | 7.8 | 8.5 | 7.8 | 8.2 | 7.2 | 7.6 | 7 | 7.5 | 7.2 | 7.2 | 7.4 | 7 | 7.6 | 6.2 | 7.2 | 5.7 | 6.3 | 4.6 | 6.2 | 7.6 | 5.2 | 5.2 | 6.4 | 5.4 | 5
Spare Capacity | 10 | % | Area of Cable | 54.1061 | 47.7836 | 56.745 | 47.7836 | 52.8102 | 40.715 | 45.3646 | 38.4845 | 44.1786 | 40.715 | 40.715 | 43.0084 | 38.4845 | 45.3646 | 30.1907 | 40.715 | 25.5176 | 31.1725 | 16.619 | 30.1907 | 45.3646 | 21.2372 | 21.2372 | 32.1699 | 22.9022 | 19.635
Area of Containment | 491 | mm² | Number of Cables | 2 | 3 | 2 | 3 | 2 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 4 | 3 | 5 | 3 | 6 | 5 | 10 | 5 | 3 | 7 | 7 | 5 | 7 | 8
Usable area | 179 | mm²
Only edit blue cells
| This spreadsheet is for information only. Based on BS EN 50174 | [8 empty] | Rev 9: January 2023
NOTE: Correct at time of publication.

## Separation Distances
Separation Distances | [5 empty] | a | b | c | d
This spreadsheet offers guidance for the general separation distances required between copper data cabling and mains power to mitigate the effects of Electromagnetic Interference (EMI). The installer shall additional ensure that all local and national legislation reagading electrical separation shall be complied with. |  |  |  | Segregation Classification - Cable |  | None | Open metalic containment | Perforated metalic containment | Solid metalic containment
[6 empty] | 1 | 2 | 3 | 4
Only edit blue cells (drop down) | [5 empty] | Applicable to plastic containment | Equivalent to weld mesh 50 mm x 100 mm and steel tray of less than 1 mm thickness (and trunking without lid). | Equivalent to steel tray of 1 mm thickness (and trunking without lid). Cables to be installed at least 10 mm below top of barrier. | Equivalent to steel conduit 1.5mm wall thickness. Steel conduit less than 1.5mm thickness will require greater separation.
Reference: EN 50174-2:2018 |  |  |  | Coaxial | 1 | 300 | 225 | 150 | 0
|  |  |  | Unscreened - Cat 5e, 6, 6a | 2 | 100 | 75 | 50 | 0
|  |  |  | Screened - Cat 5e, 6, 6a | 3 | 50 | 38 | 25 | 0
Data cable type | Unscreened - Cat 5e, 6, 6a | Please see note ** below | 2 | Cat 7 & 7a | 4 | 10 | 8 | 5 | 0
[6 empty] | Coaxial | Unscreened - Cat 5e, 6, 6a | Screened - Cat 5e, 6, 6a | Cat 7 & 7a
[6 empty] | 1 | 2 | 3 | 4
Note
Containment (applied to Data or Power cabling) | Open metalic containment | Equivalent to weld mesh 50 mm x 100 mm and steel tray of less than 1 mm thickness (and trunking without lid). | 2 | Qty of Power Circuits | P
|  |  |  | 1 to 3 | 0.2
|  |  |  | 4 to 6 | 0.4
|  | Note |  | 7 to 9 | 0.6
Quantity of Power Circuits | 1 to 3 | 3-phase cables shall be treated as 3 off 1-phase cables. | 0.2 | 10 to 12 | 0.8
|  | More than 20 A shall be treated as multiples of 20 A. |  | 13 to 15 | 1
|  | Lower voltage AC or DC power supply cables shall be treated based upon the their current ratings, i.e. a 100 A 100 V DC cable = 5 of 20 A cables |  | 16 to 30 | 2
|  |  |  | 31 to 45 | 3
|  |  |  | 46 to 60 | 4
|  |  |  | 61 to 75 | 5
Minimum separation distance | 15 mm |  |  | > 75 | 6
Only edit blue cells (drop down)
This spreadsheet is for information only. Based on EN 50174-2:2018 |  | Rev 6: October 2018
**Note: Cat 7 and 7a cables relate to Type 1 for Coupling Attenuation, as referenced in IEC61156-5 ed.2.1, which is two forms of screening media such as a foil and a braid (not two foils) 100-914 Category 6A S/FTP also meets this requirement